## Sheet1
Loop No | Oscillatory? | Noisy | Disturbance | Variance | Variance Level | Sticky Valve probability (%) | First Inference | Second Inference
12 | No oscillation | No noise | No disturbance | 1.5131 | Medium | 24.0135 | High process variability (PV std: 1.513) appears driven by setpoint changes (SP std: 1.34). Normal operation if tracking requirements. Otherwise, reduce SP variation frequency. | Poor setpoint tracking (MAE: 0.552) with weak error-OP correlation. Controller not responding appropriately to errors. Check controller mode (manual vs auto) or tune integral action.
101 | Mild oscillation | May be Noisy | No disturbance | 0.043124 | Low | 69.4956 | Moderate-to-high stiction risk (69%) with some valve sticking. Recommendation: Schedule valve maintenance before performance degrades further. | Moderate measurement noise present (high-freq ratio: 0.01). Consider adding exponential smoothing or low-pass filtering to PV signal.
131 | Mild oscillation | No noise | No disturbance | 0.025658 | Low | 83.7711 | Moderate-to-high stiction risk (84%) with some valve sticking. Recommendation: Schedule valve maintenance before performance degrades further. | Low-frequency oscillations detected (period ≈ 127 samples). Suggests process transport delay or slow dynamics. Recommendation: Review process model and consider adding derivative action.
77 | No oscillation | No noise | No disturbance | 0.055111 | Low | 32.862 | Early-stage stiction detected (33%, 13% flat OP periods). Preventive maintenance recommended to avoid future oscillations.